SRC-001: Site Readiness Checklist

Complete all items below and return signed copy to Allodial prior to scheduled delivery.

This checklist confirms the customer site meets minimum requirements for Allodial V1 deployment. Delivery will not proceed until all applicable items are verified and signed. Failure to meet site requirements may result in rescheduling fees.

Customer: ________________________________     Site Address: ________________________________

Product Tier:  [ ] Sentinel     [ ] Bastion     Scheduled Delivery: ______________

| REQUIREMENT | SENTINEL | BASTION | ✓ |
| --- | --- | --- | --- |
| ELECTRICAL |  |  |  |
| Dedicated Circuit | 120V / 15A (NEMA 5-15) | 208V / 30A (NEMA L6-30) x2 for redundant PSU | ☐ |
| UPS / Surge Protection | Recommended (650W+ capacity) | Required (1,400W+ capacity per circuit) | ☐ |
| Generator Backup | Optional | Recommended for production deployments | ☐ |
| Circuit Breaker Access | Standard panel access | Labeled and accessible within 50ft of unit | ☐ |
| PHYSICAL SPACE |  |  |  |
| Form Factor | Desktop/tower (7.6 x 18.2 x 25.5 in) | 2U rackmount (17.2 x 3.4 x 28.5 in) | ☐ |
| Placement | Desk, table, or floor (level surface) | Standard 19-inch rack, 2U of vertical space | ☐ |
| Clearance | 6 in rear clearance for airflow | Front-to-rear airflow; do not block intake/exhaust | ☐ |
| Weight Capacity | ~60 lbs | ~80 lbs + rack rail weight | ☐ |
| Physical Security | Standard office lock recommended | Locked server room or cage required | ☐ |
| ENVIRONMENTAL |  |  |  |
| Ambient Temperature | 10-35°C (50-95°F) | 10-35°C (50-95°F) | ☐ |
| Humidity | 20-80% non-condensing | 20-80% non-condensing | ☐ |
| Cooling | Standard office HVAC sufficient | Server room HVAC: 4,800+ BTU/hr available | ☐ |
| Noise Tolerance | ~35 dBA (office-safe) | ~55 dBA (server room; not office-suitable) | ☐ |
| NETWORK |  |  |  |
| Ethernet Drop | 1x RJ45 (10GbE capable) within 15ft | 1x SFP28 (25GbE) or RJ45 (10GbE fallback) | ☐ |
| DHCP or Static IP | 1x IPv4 address reserved | 1x IPv4 address reserved + 1x BMC/IPMI | ☐ |
| Firewall / VLAN | Isolate on dedicated VLAN (recommended) | Isolate on dedicated VLAN (required) | ☐ |
| Internet Access | Not required (Network-Isolated Mode standard) | Not required (Network-Isolated Mode standard) | ☐ |
| DNS / NTP | Internal DNS/NTP if LAN-connected | Internal DNS/NTP if LAN-connected | ☐ |
| PERSONNEL |  |  |  |
| IT Contact (primary) | Name + phone + email on file with Allodial | Name + phone + email on file with Allodial | ☐ |
| IT Contact (backup) | Recommended | Required | ☐ |
| Receiving Logistics | Confirm loading dock or delivery access | Confirm loading dock, rack tools, and rail installation capability | ☐ |
| Training Attendees | 1-2 staff for 2-hour onboarding session | 2-4 staff for 4-hour onboarding session | ☐ |

SITE READINESS CERTIFICATION

I certify that the site identified above meets all checked requirements for the product tier selected. I understand that Allodial will verify these conditions upon arrival, and that failure to meet stated requirements may result in deployment delay and applicable rescheduling fees.

Customer Signature: ________________________________     Date: ______________

Customer Name (printed): ________________________________     Title: ______________

Allodial Site Engineer: ________________________________     Date: ______________